ADW300-LoRaWAN Configuration Instructions

V1.2

2025.08

Documentation version change log table

| Version Number | Release Date | Change Summary | Notes |
| --- | --- | --- | --- |
| V1.0 | 2024-07 | Initial release |  |
| V1.1 | 2024-11-29 | Corrected the issue with the primary and secondary value address table; Corrected the issue with the decoder incorrectly recognizing CS byte. | Please note that some primary and secondary value addresses have been swapped. |
| V1.2 | 2025-0818 | Simplify the information, update the software configuration instructions, and update the decoder |  |

catalogue

ADW300-LoRaWAN Configuration Instructions	1

1 Fast-Connect Settings Guide	3

2 Connect the meter	4

2.1 Connect the meter through RS485.	4

2.2 Communicate with meter using ADW300.exe .	4

3 Configure on the “LoRaWAN Parameter” page.	5

3.1 LoRaWAN info	5

3.1.1 DEVEUI	5

3.1.2 BAND	6

3.2 LoRaWAN Setting	7

3.2.1 APPEUI、APPKEY、Upload Interval	8

3.2.2 DataRate	8

3.3 Channel Setting	10

3.4 Packet Type	10

3.5 Updata Setting	11

3.5.1 Set the data to be uploaded	12

3.5.2 Num in Updata Setting	17

3.5.3 Need CS	18

3.5.4 Big endian	19

3.5.5 Updata in sec	20

4 Payload format.	21

4.1 Selectable Data Packet	21

4.1.1 Default field template	21

4.1.2 HEX format	21

4.1.3 Data list	22

4.1.4 Decoder for the initial template	25

4.2 Fixed Packet Of 2526	25

5 Complete address table	25

5.1 Secondary Data Part 1	26

5.2 Secondary Value Part 2	36

5.3 Primary Value (Real Value) Part 1	41

5.4 Primary Value (Real Value) Part 2	42

Fast-Connect Settings Guide

| Parameter | OTAA Default | Where to Change ( Chapter) |
| --- | --- | --- |
| Region | CN470, RU868, IN865, EU868, US915, AU915, KR920, AS923_1, AS923_2, AS923_3, AS923_4 | 3.1.2 |
| DevEUI | Label on the front of the meter. | Not writable, but readable 3.1.1 |
| Join EUI / AppEUI | 1122334455667788 | 3.2.1 |
| AppKey (OTAA) | 11223344556677881122334455667788 | 3.2.1 |
| NwkSKey / AppSKey (ABP) | - | - |
| Data Rate | DR4 (DR3 for US915) | 3.2.2 |
| TX Power | 16 dBm | - |
| Channel Mask | 0-7 enabled | 3.3 |
| Max Payload (bytes) | 220 bytes | 3.2.2 |
| Data List | Default template | 4.1.3 |

LoRaWAN version (≥ 1.0.3) is supported.

The uploaded data has a default template, and the decoder :

Connect the meter

Connect the meter through RS485.

Connect meter to a computer using an RS485 to USB converter.

The + sign on meter is connected to 21 port , and the – sign on meter is connected to 22 port.

For example:

Then the meter should be powered through the power lines L (port 1) and N (port 2).

Communicate with meter using ADW300.exe .

ADW300 configuration software EN T version 1.1 and above are recommended

Configure on the “LoRaWAN Parameter” page.

LoRaWAN info

DEVEUI

Read the LoRaWAN Device EUI from the meter.

*At the same time, the firmware version number is read out for reference only when engineers debug, where the number has nothing to do with the actual operating frequency band of the module.

BAND

Region / Band Plan: RU868, IN865, EU868, US915, AU915, KR920, AS923_1, AS923_2, AS923_3, AS923_4.

LoRaWAN Setting

APPEUI、APPKEY、Upload Interval

They have an initial value at the factory, usually：

APPEUI：1122334455667788

APPKEY：11223344556677881122334455667788

Ramdom APPKEY : A random APPKEY value can be obtained.

Upload Interval (The time interval between data uploads)：1

Default unit : minute, can be change to second (at least 5 sec).

They can all be set to the desired number. Read the data before setting it.

DataRate

The default DataRate is DR4. Due to the need to upload fixed length packets, ADR is disabled in the module, so we need to set a data transfer rate level that the module can recognize, which is DataRate. After setting, the corresponding spread spectrum factor is fixed, and the maximum length of data that can be sent per packet is fixed.

The maximum data load (unit: byte) of a single packet for each DataRate in each frequency band：

|  | CN470 | EU868 | AU915 | US915 | AS923 |
| --- | --- | --- | --- | --- | --- |
| DR0 | 50 | 50 | 50 | 10 | 50 |
| DR1 | 50 | 50 | 50 | 50 | 50 |
| DR2 | 50 | 50 | 50 | 110 | 50 |
| DR3 | 110 | 110 | 110 | 220 | 110 |
| DR4 | 220 | 220 | 220 | - | 220 |
| DR5 | 220 | 220 | 220 | - | 220 |

The larger the DataRate Number, the smaller the spread factor and the shorter the transmission time, the more data information is transmitted per unit time, but the anti-interference ability is reduced, so the transmission distance is shortened.

On the contrary, you can improve the anti-interference of the transmission by setting a smaller DataRate, and extend the transmission distance, and he packet may be divided into more packets to be sent, depending on the corresponding single packet maximum load.

*The maximum DataRate Level corresponding to the US915 is DR3.

Channel Setting

In general, the number of channels is set to 0, which means that the module will run on default channels within the Region / Band Plan.

Set the corresponding channel frequencies and the number of channels as needed. By default, for channels 0-7, the reading will not display the default values

A maximum of 8 channels can be configured. Start channel 922.2MHz, which can be set to 922200000. Enable 8 channels starting from 922200000.

Packet Type

Click Read to view the data packet mode currently in use.

Selectable Data Packet：Default mode. In this mode, there is a default data template available for upload. It can also be customized. The information in "Updata Setting" is the data template.

Fixed Packet of 2526：Special template, upload data is fixed. In this mode, updata settings cannot be modified.

Updata Setting

This is the setting of what data the meter uploads. You can select the required data fields according to the complete address table, all the start address and register length can be found in the complete address table. We can choose to upload the secondary value or the primary value(real value). Or use the default field template. The following is a description of the Updata Settings.

Set the data to be uploaded

Select adjacent parameters

When we want to upload the data include PT、CT、Temperature of N phase. We first find the position of the parameter in the data table, like this PT, whose start address is 14. The next one is CT, start address is 15. And then Temperature of N phase, start address is 16.

You can see that after the name of the parameter in the table is the number of bytes, this value divided by 2 is the size of the register occupied by the parameter.

2 (bytes) / 2 = 1 (register),

4 (bytes) / 2 = 2 (register).

From 14 to 16, there are 3 registers.

So when we set a group of the data, we fill in the start address first, the address is 14. And then the register length, which is 3. So that the three parameters selected will be added to the package in order.

Select parameters that are not adjacent

A group of data must be in adjacent states. When you need non-adjacent data, you can set it in different groups.

When we want the data include UA、UB、UC、UAB、UBC、UCA、IA、IB、IC. But they are not adjacent to the n-phase temperature parameter, so we need to set it to the new group.

So we find the start address is 20, Each data account for 1 register, so there are 9 registers in total. Then we set like :

Selects data that occupies two registers

When we need more parameters such as Active power of A phase, it may be involved that some data is 4 bytes in the address table, that is, 2 registers, which is twice the size of the normal data. We just need to calculate the total number of registers that this set of data actually occupies.

As shown in the table, we need these data, some data account for 4 bytes, and some data account for 2 bytes, converted to the number of registers, the sum can be 29 registers. So we fill in the start address and the number of registers as follows:

Num in Updata Setting

Num is the number of valid data groups. There are a total of 20 groups that can be filled in, and after filling in the required data group, fill in the rest of the 0.

Finally set the total number of groups. Like the picture, there are 9 groups of data, so set num 9.

If the num value is less than the total number of data groups you entered, for example, we entered 9 groups here, but if num only enter 1, only the first set of data will be uploaded in the data packet. The packet only includes PT、CT、Temperature of N phase. No other data will be uploaded.

* The byte size or number of registers that data represents in the data address table does not represent the byte length that data will occupy when it is finally uploaded. Whether the selected data is originally 2 bytes or 4 bytes, it is unified to 5 bytes per parameter (1 sequence number +4 bytes of data) when uploaded.

Need CS

Enable to add a CS checksum byte to the end of the uploaded data packet.

This option is selected by default for the initial template

Checksum: All the data in the uploaded packet is added to obtain a value, and then the value is divided by 256 to obtain a remainder, which is the CS checksum.

For example, a packet contains this data:

01 00 00 00 01 02 00 00 00 01

If we need CS, then the CS checksum is added to the end:

01 00 00 00 01 02 00 00 00 01 05

So in the absence of CS, the packet size is a multiple of 5. If we add CS it's a multiple of 5, plus 1 byte.

The function of CS checksum calculation is constructed by C language:

//pBus[] is the data buffer.

// start is the location of the first data.

// n is the number of bytes computed.

uint8_t CS16(uint8_t* pBus, uint16_t start, uint16_t n)

{

Uint16_t i;

uint8_t sum = 0;

for (i = start ; i < n+start ; i++)

{

sum = ( sum + pBus[i] ) % 256;

}

return sum;

}

Big endian

Select whether we want big endian.

This option is selected by default for the initial template.

If we upload a parameter with a value of 0x12345678, then in the big endian condition it looks like this:

num   value

01    12 34 56 78

In the small endian condition it looks like this:

num   value

01    78 56 34 12

Updata in sec

After this function is enabled, the data upload frequency changes from minute to second. For example, the original data frequency was 5, and the data was uploaded every 5 minutes. After the second level upload was enabled, the data was uploaded every 5 seconds.

It is not selected by default. If you need to use it, consult engineers first.

Payload format.

Selectable Data Packet

By default, or by selection, the packet type is Selectable Data Packet. In this mode, there is an initial template, and we can also customize it.

Default field template

The initial template contains a total of 9 data groups, including 68 parameters and 1 CS checksum. The data is in big endian.

HEX format

04                             00 00 08 98  (=2200)

Number (1 byte)     +    Data Value (4 bytes)

All parameters have 4 bytes of space in the packet, but the data type may be int16, uint16, int32, uint32, float. What is the specific type of the value of each parameter according to the data list or address table.

There is a checksum at the last of all data.

Uploaded data:

01 00 00 00 01 02 00 00 00 01 03 00 00 00 00 04 00 00 00 00 05 00 00 00 00 06 00 00 00 00 07 00 00 00 00 08 00 00 00 00 09 00 00 00 00 0A 00 00 00 01 0B 00 00 00 01 0C 00 00 00 01 0D 00 00 00 00 0E 00 00 00 00 0F 00 00 00 00 10 00 00 00 00 11 00 00 00 00 12 00 00 00 00 13 00 00 00 00 14 00 00 00 00 15 00 00 00 00 16 00 00 00 00 17 00 00 00 00 18 00 00 00 00 19 00 00 03 E8 1A 00 00 03 E8 1B 00 00 03 E8 1C 00 00 03 E8 1D 00 00 00 00 1E 00 00 00 00 1F 00 00 00 00 20 00 00 00 00 21 00 00 00 00 22 00 00 00 00 23 00 00 00 00 24 00 00 00 00 25 00 00 00 00 26 00 00 00 00 27 00 00 00 00 28 00 00 00 00 29 00 00 00 00 2A 00 00 00 00 2B 00 00 00 00 2C 00 00 00 00 2D 00 00 00 00 2E 00 00 00 00 2F 00 00 00 00 30 00 00 00 00 31 00 00 00 00 32 00 00 00 00 33 00 00 00 00 34 00 00 00 00 35 00 00 00 00 36 00 00 00 00 37 00 00 00 00 38 00 00 00 00 39 00 00 00 00 3A 00 00 00 00 3B 00 00 00 00 3C 00 00 00 00 3D 00 00 00 00 3E 00 00 00 00 3F 00 00 00 00 40 00 00 00 00 41 00 00 00 00 42 00 00 00 00 43 00 00 00 00 44 00 00 00 00 9E

Notice : Mostly data are secondary side values from the meter. Need to deal data for getting real value.

Data list

The following table lists the data for the initial template. And the table explains how to process the secondary value data to obtain the primary value(real value) data:

| Num in packet (Hex) | Variable | Data type | Unit | Notes |
| --- | --- | --- | --- | --- |
| 01 | PT | Uint16 | 1 |  |
| 02 | CT | Uint16 | 1 |  |
| 03 | Temperature of N phase | Int16 | 0.1℃ | If the reading value is 105, the temperature is 10.5℃ |
| 04 | Voltage of A phase | Uint16 | 0.1V | If U=2200，PT=1; then U=U*PT=2200*0.1*1=220.0V |
| 05 | Voltage of B phase | Uint16 | 0.1V |  |
| 06 | Voltage of C phase | Uint16 | 0.1V |  |
| 07 | Voltage between A-B | Uint16 | 0.1V |  |
| 08 | Voltage between B-C | Uint16 | 0.1V |  |
| 09 | Voltage between C-A | Uint16 | 0.1V |  |
| 0A | Current of A phase | Uint16 | 0.01A | If I=200，CT=10; then I=I*CT =200*0.01*10=20A |
| 0B | Current of B phase | Uint16 | 0.01A |  |
| 0C | Current of C phase | Uint16 | 0.01A |  |
| 0D | Active power of A phase | int32 | 0.001kW | If value=11720， PT=10,CT=10; then value=value*PT*CT= 11720*0.001*10*10=1172.0 kW |
| 0E | Active power of B phase | Int32 | 0.001kW |  |
| 0F | Active power of C phase | Int32 | 0.001kW |  |
| 10 | Total active power | Int32 | 0.001kW |  |
| 11 | Reactive power of A phase | Int32 | 0.001kVar | If value=11720， PT=10,CT=10; then value=value*PT*CT= 11720*0.001*10*10=1172.0 kVar |
| 12 | Reactive power of B phase | Int32 | 0.001kVar |  |
| 13 | Reactive power of C phase | Int32 | 0.001kVar |  |
| 14 | Total reactive power | Int32 | 0.001kVar |  |
| 15 | Apparent power of A phase | Uint32 | 0.001kVA | If value=11720， PT=10,CT=10; then value=value*PT*CT= 11720*0.001*10*10=1172.0 kVA |
| 16 | Apparent power of B phase | Uint32 | 0.001kVA |  |
| 17 | Apparent power of C phase | Uint32 | 0.001kVA |  |
| 18 | Total apparent power | Uint32 | 0.001kVA |  |
| 19 | Power factor of A phase | Uint16 | 0.001 | If value=999, then value=999*0.001=0.999 |
| 1A | Power factor of B phase | Uint16 | 0.001 |  |
| 1B | Power factor of C phase | Uint16 | 0.001 |  |
| 1C | Total power factor | Uint16 | 0.001 |  |
| 1D | State of DI | Uint16 | 0 or 1 | Bit0：DI1 Bit1：DI2 Bit2：DI3 Bit3：DI4 |
| 1E | Total energy consumption | Uint32 | 0.01 kWh | If value=120201， PT=10,CT=10;then value=value*PT*CT= 120201*0.01*10*10=120201 kWh |
| 1F | Forward active energy consumption | Uint32 | 0.01 kWh |  |
| 20 | Reversing active energy consumption | Uint32 | 0.01 kWh |  |
| 21 | Forward reactive energy consumption | Uint32 | 0.01 kVarh | If value=120201， PT=10,CT=10;then value=value*PT*CT= 120201*0.01*10*10=120201 kVarh |
| 22 | Reversing reactive energy consumption | Uint32 | 0.01 kVarh |  |
| 23 | Total energy consumption on A phase | Uint32 | 0.01 kWh | If value=120201， PT=10,CT=10;then value=value*PT*CT= 120201*0.01*10*10=120201 kWh |
| 24 | Forward active energy consumption on A phase | Uint32 | 0.01 kWh |  |
| 25 | Reversing active energy consumption on A phase | Uint32 | 0.01 kWh |  |
| 26 | Forward reactive energy consumption on A phase | Uint32 | 0.01 kVarh | If value=120201， PT=10,CT=10;then value=value*PT*CT= 120201*0.01*10*10=120201 kVarh |
| 27 | Reversing reactive energy consumption on A phase | Uint32 | 0.01 kVarh |  |
| 28 | Total energy consumption on B phase | Uint32 | 0.01 kWh | If value=120201， PT=10,CT=10;then value=value*PT*CT= 120201*0.01*10*10=120201 kWh |
| 29 | Forward active energy consumption on B phase | Uint32 | 0.01 kWh |  |
| 2A | Reversing active energy consumption on B phase | Uint32 | 0.01 kWh |  |
| 2B | Forward reactive energy consumption on B phase | Uint32 | 0.01 kVarh | If value=120201， PT=10,CT=10;then value=value*PT*CT= 120201*0.01*10*10=120201 kVarh |
| 2C | Reversing reactive energy consumption on B phase | Uint32 | 0.01 kVarh |  |
| 2D | Total energy consumption on C phase | Uint32 | 0.01 kWh | If value=120201， PT=10,CT=10;then value=value*PT*CT= 120201*0.01*10*10=120201 kWh |
| 2E | Forward active energy consumption on C phase | Uint32 | 0.01 kWh |  |
| 2F | Reversing active energy consumption on C phase | Uint32 | 0.01 kWh |  |
| 30 | Forward reactive energy consumption on C phase | Uint32 | 0.01 kVarh | If value=120201， PT=10,CT=10;then value=value*PT*CT= 120201*0.01*10*10=120201 kVarh |
| 31 | Reversing reactive energy consumption on C phase | Uint32 | 0.01 kVarh |  |
| 32 | Maximum forward active demand in current month | Uint32 | 0.001 KW | If value=11202,PT=10,CT=10; then value=value*PT*CT= 11202*0.001*10*10=1120.2 kW |
| 33 | Occur time | Uint32 |  | Minute, hour, day, month |
| 34 | THDUa | Uint16 | 0.01 | Total distortion rate of voltage and current on each phase If value= 2425,then value=2425*0.01=25.24% |
| 35 | THDUb | Uint16 | 0.01 |  |
| 36 | THDUc | Uint16 | 0.01 |  |
| 37 | THDIa | Uint16 | 0.01 |  |
| 38 | THDIb | Uint16 | 0.01 |  |
| 39 | THDIc | Uint16 | 0.01 |  |
| 3A | Current forward active demand | Uint32 | 0.001 KW | If value=11720， PT=10,CT=10; then value=value*PT*CT= 11720*0.001*10*10=1172.0 kW |
| 3B | Voltage imbalance | Uint16 | 0.01% | If value=2201, then value= 2201*0.01=22.01% |
| 3C | Current imbalance | Uint16 | 0.01% |  |
| 3D | Temperature on A phase | Int16 | 0.1℃ |  |
| 3E | Temperature on B phase | Int16 | 0.1℃ |  |
| 3F | Temperature on C phase | Int16 | 0.1℃ |  |
| 40 | Current total spike active energy | Uint32 | 0.01 kWh | If value=120201， PT=10,CT=10;then value=*PT*CT= 65120201*0.01*10*10=120201 kWh |
| 41 | Current total peak active energy | Uint32 | 0.01 kWh |  |
| 42 | Current total flat active energy | Uint32 | 0.01 kWh |  |
| 43 | Current total valley active energy | Uint32 | 0.01 kWh |  |
| 44 | Aftercurrent | Uint16 | 1 mA | If I=20，CT=10; then I=I*CT=20*10=200mA |

Decoder for the initial template

Fixed Packet Of 2526

In this mode, there is a special data template and it cannot be changed. It is a retention of the old version template. This will not be elaborated here.

Complete address table

If you want to freely define the content of the uploaded data, you can select the data groups from the following tables.

Description of the table :

- The first column is the start address in hexadecimal.

- The second column is the start address in decimal.

- The third column is variable name.

- The fourth column is data length (divide by 2 to get the number of register stored).

- The fifth column indicates whether the data is readable or writable.

- The sixth column describes the data type, decimal cases, and how to deal the data.

Secondary Data Part 1

Table 1. secondary data

| Start Address (Hexadecimal) | Start Address （Decimal） | Variable | Length (Bytes) | R/W | Notes |
| --- | --- | --- | --- | --- | --- |
| 0000H | 0 | Address | 2 | R/W | 1～247 |
| 0001H | 1 | Baud rate | 2 | R/W | 1：1200bps 2：3400bps 3：4800bps 4：9600bps |
| 0002H | 2 | Spreading factor | 2 | R/W | 6~12 |
| 0003H | 3 | Frequency channel setting | 2 | R/W | 0-45 (Communication with the same frequency host) |
| 0004H | 4 | High byte: parity mode, low byte: stop Bit | 2 | R/W | High byte: 0-none, 1-even, 2-odd; low byte: 0- 1 stop Bit, 1- 2 stop Bit |
| 0005H-0006H | 5-6 | Reserved |  |  |  |
| 0007H | 7 | Backlight Time |  |  |  |
| 0008H | 8 | Code |  |  |  |
| 0009H~000CH | 9-13 | Reserved |  |  |  |
| 000EH | 14 | PT |  |  |  |
| 000FH | 15 | CT |  |  |  |
| 0010H | 16 | Temperature of N phase | 2 | R | Int16 unit 0.1℃ If the reading value is 105, the temperature is 10.5℃ |
| 0011H~0013H | 17-19 | Time, date (second, minute, hour, day, month, year) |  |  |  |
| 0014H | 20 | Voltage of A phase | 2 | R | Uint16 1 decimal places Unit V If U=2200，PT=1; then U=U*PT=2200*0.1*1=220.0V |
| 0015H | 21 | Voltage of B phase | 2 | R |  |
| 0016H | 22 | Voltage of C phase | 2 | R |  |
| 0017H | 23 | Voltage between A-B | 2 | R |  |
| 0018H | 24 | Voltage between B-C | 2 | R |  |
| 0019H | 25 | Voltage between C-A | 2 | R |  |
| 001AH | 26 | Current of A phase | 2 | R | Uint16 unit A 2 decimal places If I=200，CT=10; then I=I*CT=200*0.01*10=20A |
| 001BH | 27 | Current of B phase | 2 | R |  |
| 001CH | 28 | Current of C phase | 2 | R |  |
| 001DH | 29 | Vector sum of 3-phase current | 2 | R |  |
| 001EH | 30 | Active power of A phase | 4 | R | Int32 unit kW 3 decimal places If value=11720， PT=10,CT=10; then value=value*PT*CT= 11720*0.001*10*10=1172.0 kW |
| 0020H | 32 | Active power of B phase | 4 | R |  |
| 0022H | 34 | Active power of C phase | 4 | R |  |
| 0024H | 36 | Total active power | 4 | R |  |
| 0026H | 38 | Reactive power of A phase | 4 | R | Int32 unit kVar 3 decimal places If value=11720， PT=10,CT=10; then value=value*PT*CT= 11720*0.001*10*10=1172.0 kVar |
| 0028H | 40 | Reactive power of B phase | 4 | R |  |
| 002AH | 42 | Reactive power of C phase | 4 | R |  |
| 002CH | 44 | Total reactive power | 4 | R |  |
| 002EH | 46 | Apparent power of A phase | 4 | R | Uint32 unit kVA 3 decimal places If value=11720， PT=10,CT=10; then value=value*PT*CT= 11720*0.001*10*10=1172.0 kVA |
| 0030H | 48 | Apparent power of B phase | 4 | R |  |
| 0032H | 50 | Apparent power of C phase | 4 | R |  |
| 0034H | 52 | Total apparent power | 4 | R |  |
| 0036H | 54 | Power factor of A phase | 2 | R | Uint16 3 decimal places If value=999, then value=999*0.001=0.999 |
| 0037H | 55 | Power factor of B phase | 2 | R |  |
| 0038H | 56 | Power factor of C phase | 2 | R |  |
| 0039H | 57 | Total power factor | 2 | R |  |
| 003AH | 58 | State of DI | 2 | R | Uint16 Bit0：DI1 Bit1：DI2 Bit2：DI3 Bit3：DI4 |
| 003BH | 59 | Frequency of power | 2 | R | Uint16 2 decimal places If value=5000,then value=5000*0.01=50.00HZ |
| 003CH | 60 | Total energy consumption | 4 | R | Uint32 unit kWh 2 decimal places If value=120201， PT=10,CT=10;then value=value*PT*CT= 120201*0.01*10*10=120201 kWh |
| 003EH | 62 | Forward active energy consumption | 4 | R |  |
| 0040H | 64 | Reversing active energy consumption | 4 | R |  |
| 0042H | 66 | Forward reactive energy consumption | 4 | R | Uint32 unit kVarh 2 decimal places If value=120201， PT=10,CT=10;then value=value*PT*CT= 120201*0.01*10*10=120201 kVarh |
| 0044H | 68 | Reversing reactive energy consumption | 4 | R |  |
| 0046H | 70 | Total energy consumption on A phase | 4 | R | Uint32 unit kWh 2 decimal places If value=120201， PT=10,CT=10;then value=value*PT*CT= 120201*0.01*10*10=120201 kWh |
| 0048H | 72 | Forward active energy consumption on A phase | 4 | R |  |
| 004AH | 74 | Reversing active energy consumption on A phase | 4 | R |  |
| 004CH | 76 | Forward reactive energy consumption on A phase | 4 | R | Uint32 unit kVarh 2 decimal places If value=120201， PT=10,CT=10;then value=value*PT*CT= 120201*0.01*10*10=120201 kVarh |
| 004EH | 78 | Reversing reactive energy consumption on A phase | 4 | R |  |
| 0050H | 80 | Total energy consumption on B phase | 4 | R | Uint32 unit kWh 2 decimal places If value=120201， PT=10,CT=10;then value=value*PT*CT= 120201*0.01*10*10=120201 kWh |
| 0052H | 82 | Forward active energy consumption on B phase | 4 | R |  |
| 0054H | 84 | Reversing active energy consumption on B phase | 4 | R |  |
| 0056H | 86 | Forward reactive energy consumption on B phase | 4 | R | Uint32 unit kVarh 2 decimal places If value=120201， PT=10,CT=10;then value=value*PT*CT= 120201*0.01*10*10=120201 kVarh |
| 0058H | 88 | Reversing reactive energy consumption on B phase | 4 | R |  |
| 005AH | 90 | Total energy consumption on C phase | 4 | R | Uint32 unit kWh 2 decimal places If value=120201， PT=10,CT=10;then value=value*PT*CT= 120201*0.01*10*10=120201 kWh |
| 005CH | 92 | Forward active energy consumption on C phase | 4 | R |  |
| 005EH | 94 | Reversing active energy consumption on C phase | 4 | R |  |
| 0060H | 96 | Forward reactive energy consumption on C phase | 4 | R | Uint32 unit kVarh 2 decimal places If value=120201， PT=10,CT=10;then value=value*PT*CT= 120201*0.01*10*10=120201 kVarh |
| 0062H | 98 | Reversing reactive energy consumption on C phase | 4 | R |  |
| 0064H | 100 | Maximum forward active demand in current month | 4 | R | Uint32 unit KW 3 decimal places If value=11202,PT=10,CT=10; then value=value*PT*CT= 11202*0.001*10*10=1120.2 kW |
| 0066H~0067H | 102-103 | Occur time | 4 | R | Minute, hour, day, month |
| 0068H | 104 | Maximum reversing active demand in current month | 4 | R | Uint32 unit kVar 3 decimal places If value=11202,PT=10,CT=10; then value=value*PT*CT= 11202*0.001*10*10=1120.2 kVar |
| 006AH~006BH | 106-107 | Occur time | 4 | R | Minute, hour, day, month |
| 006CH | 108 | Maximum forward reactive demand in current month | 4 | R | Uint32 unit kVar 3 decimal places If value=11202,PT=10,CT=10; then value=value*PT*CT= 11202*0.001*10*10=1120.2 kVar |
| 006EH~006FH | 110-111 | Occur time | 4 | R | Minute, hour, day, month |
| 0070H | 112 | Maximum reversing reactive demand in current month | 4 | R | Uint32 unit kVar 3 decimal places If value=11202,PT=10,CT=10; then value=value*PT*CT= 11202*0.001*10*10=1120.2 kVar |
| 0072H~0073H | 114-115 | Occur time | 4 | R | Minute, hour, day, month |
| 0074H | 116 | THDUa | 2 | R | Total distortion rate of voltage and current on each phase Uint16 2 decimal places If value= 2425,then value=2425*0.01=25.24% |
| 0075H | 117 | THDUb | 2 | R |  |
| 0076H | 118 | THDUc | 2 | R |  |
| 0077H | 119 | THDIa | 2 | R |  |
| 0078H | 120 | THDIb | 2 | R |  |
| 0079H | 121 | THDIc | 2 | R |  |
| 007AH | 122 | THUa(Harmonic on 2nd-31st) | 2×30 | R | Harmonic voltage on 2nd-31st Uint16 2 decimal places If value= 2425,then value=2425*0.01=25.24% |
| 0098H | 152 | THUa(Harmonic on 2nd-31st) | 2×30 | R |  |
| 00B6H | 182 | THUb(Harmonic on 2nd-31st) | 2×30 | R |  |
| 00D4H | 212 | THUc(Harmonic on 2nd-31st) | 2×30 | R | Harmonic current on 2nd-31st Uint16 2 decimal places If value= 2425,then value=2425*0.01=25.24% |
| 00F2H | 242 | THIa(Harmonic on 2nd-31st) | 2×30 | R |  |
| 0110H | 272 | THIb(Harmonic on 2nd-31st) | 2×30 | R |  |
| 012EH | 302 | Fundamental voltage on A phase | 2 | R | Uint16 unit V 1 decimal places If U=1010，PT=6; then U=U*PT=1010*0.1*6=606V |
| 012FH | 303 | Fundamental voltage on B phase | 2 | R |  |
| 0130H | 304 | Fundamental voltage on C phase | 2 | R |  |
| 0131H | 305 | Harmonic voltage on A phase | 2 | R |  |
| 0132H | 306 | Harmonic voltage on B phase | 2 | R |  |
| 0133H | 307 | Harmonic voltage on C phase | 2 | R |  |
| 0134H | 308 | Fundamental current on A phase | 2 | R | Uint16 unit A 2 decimal places If I=200，CT=10; I=I*CT=200*0.01*10=20A |
| 0135H | 309 | Fundamental current on B phase | 2 | R |  |
| 0136H | 310 | Fundamental current on C phase | 2 | R |  |
| 0137H | 311 | Harmonic current on A phase | 2 | R |  |
| 0138H | 312 | Harmonic current on B phase | 2 | R |  |
| 0139H | 313 | Harmonic current on C phase | 2 | R |  |
| 013AH | 314 | Fundamental active power on A phase | 4 | R | Int32 unit kW 3 decimal places If value=11720， PT=10,CT=10; then value=value*PT*CT= 11720*0.001*10*10=1172.0 kW |
| 013CH | 316 | Fundamental active power on B phase | 4 | R |  |
| 013EH | 318 | Fundamental active power on C phase | 4 | R |  |
| 0140H | 320 | Fundamental active power | 4 | R |  |
| 0142H | 322 | Fundamental reactive power on A phase | 4 | R | Int32 unit kVar 3 decimal places If value=11720， PT=10,CT=10; then value=value*PT*CT= 11720*0.001*10*10=1172.0 kVar |
| 0144H | 324 | Fundamental reactive power on B phase | 4 | R |  |
| 0146H | 326 | Fundamental reactive power on C phase | 4 | R |  |
| 0148H | 328 | Fundamental reactive power | 4 | R |  |
| 014AH | 330 | Harmonic active power on A phase | 4 | R | Int32 unit kW 3 decimal places If value=11720， PT=10,CT=10; then value=value*PT*CT= 11720*0.001*10*10=1172.0 kW |
| 014CH | 332 | Harmonic active power on B phase | 4 | R |  |
| 014EH | 334 | Harmonic active power on C phase | 4 | R |  |
| 0150H | 336 | Harmonic active power | 4 | R |  |
| 0152H | 338 | Harmonic reactive power on A phase | 4 | R | Int32 unit kVar 3 decimal places If value=11720， PT=10,CT=10; then value=value*PT*CT= 11720*0.001*10*10=1172.0 kVar |
| 0154H | 340 | Harmonic reactive power on B phase | 4 | R |  |
| 0156H | 342 | Harmonic reactive power on C phase | 4 | R |  |
| 0158H | 344 | Harmonic reactive power | 4 | R |  |
| 015AH | 346 | Current forward active demand | 4 | R | Uint32 unit kW 3 decimal places If value=11720， PT=10,CT=10; then value=value*PT*CT= 11720*0.001*10*10=1172.0 kW |
| 015CH | 348 | Current reversing active demand | 4 | R |  |
| 015EH | 350 | Current forward reactive demand | 4 | R | Uint32 unit kVar 3 decimal places If value=11720， PT=10,CT=10; then value=value*PT*CT= 11720*0.001*10*10=1172.0 kVar |
| 0160H | 352 | Current reversing reactive demand | 4 | R |  |
| 0162H | 354 | Voltage imbalance | 2 | R | Uint16 unit 0.01% If value=2201,then value= 2201*0.01=22.01% |
| 0163H | 355 | Current imbalance | 2 | R |  |
| 0164H | 356 | Temperature on A phase | 2 | R | Int16 unit 0.1℃ |
| 0165H | 357 | Temperature on B phase | 2 | R |  |
| 0166H | 358 | Temperature on C phase | 2 | R |  |
| 0167H | 359 | Time zone number/Time zone date: day | 2 | R/W | Time list |
| 0168H | 360 | Time zone date: month/Time zone number | 2 | R/W |  |
| 0169H | 361 | Time zone date: day/ Time zone date: month | 2 | R/W |  |
| 016AH | 362 | Time zone number/Time zone date: day | 2 | R/W |  |
| 016BH | 363 | Time zone date: month/Time zone number | 2 | R/W |  |
| 016CH | 364 | Time zone date: day/ Time zone date: month | 2 | R/W |  |
| 016DH … 0181H | 365-385 | 1-14 period of time Parameters setting information | 2 | R/W | 1# time list |
| 0182H … 0196H | 386-406 | 1-14 period of time Parameters setting information | 2 | R/W | 2# time list |
| 0197H | 407 | Current total spike active energy | 4 | R | Uint32 unit kWh 2 decimal places If value=120201， PT=10,CT=10;then value=*PT*CT= 120201*0.01*10*10=120201 kWh |
| 0199H | 409 | Current total peak active energy | 4 | R |  |
| 019BH | 411 | Current total flat active energy | 4 | R |  |
| 019DH | 413 | Current total valley active energy | 4 | R |  |
| 019FH | 415 | Current total spike forward active energy | 4 | R |  |
| 01A1H | 417 | Current total peak forward active energy | 4 | R |  |
| 01A3H | 419 | Current total flat forward active energy | 4 | R |  |
| 01A5H | 421 | Current total valley forward active energy | 4 | R |  |
| 01A7H | 423 | Current total spike reversing active energy | 4 | R |  |
| 01A9H | 425 | Current total peak reversing active energy | 4 | R |  |
| 01ABH | 427 | Current total flat reversing active energy | 4 | R |  |
| 01ADH | 429 | Current total valley reversing active energy | 4 | R |  |
| 01AFH | 431 | Current total spike forward reactive energy | 4 | R | Uint32 unit kVarh 2 decimal places If value=120201， PT=10,CT=10;then value=*PT*CT= 120201*0.01*10*10=120201 kVarh |
| 01B1H | 433 | Current total peak forward reactive energy | 4 | R |  |
| 01B3H | 435 | Current total flat forward reactive energy | 4 | R |  |
| 01B5H | 437 | Current total valley forward reactive energy | 4 | R |  |
| 01B7H | 439 | Current total spike reversing reactive energy | 4 | R |  |
| 01B9H | 441 | Current total peak reversing reactive energy | 4 | R |  |
| 01BBH | 443 | Current total flat reversing reactive energy | 4 | R |  |
| 01BDH | 445 | Current total valley reversing reactive energy | 4 | R |  |
| 01BFH | 447 | wireless signal strength | 2 | R | Int16 |
| 01C0H | 448 | Freeze time | 2 | R/W | High byte:Hour， low byte:DAY |
| 01C1H | 449 | Aftercurrent | 2 | R | Uint16 unit mA If I=20，CT=10; then I=I*CT=20*10=200mA |
| 01C2H | 450 | DO1 | 2 | R/W | Uint16 Bit0 effective |
| 01C3H | 451 | DO2 | 2 | R/W | Uint16 Bit0 effective |
| 01C4H | 452 | Demand cycle | 2 | R/W | 1：15min 2：30min 3：45min 4：60min |
| 01C5H-01CFH | 453-463 | reserved |  |  |  |
| 01D0H-01EBH | 464-491 | Related data of alarm 1, see section 6.3.1 for details |  |  |  |
| 01ECH | 492 | A phase voltage Angle | 2 | R | Uint16 2 decimal places If value= 9011, then value=9011*0.01=90.11° |
| 01EDH | 493 | B phase voltage Angle | 2 | R |  |
| 01EEH | 494 | C phase voltage Angle | 2 | R |  |
| 01EFH | 495 | reserved |  |  |  |
| 01F0H | 496 | Protocol selection bit | 2 | R/W | 0：安全用电 1：电力运维 |
| 01F2H | 498 | Real-time perceived demand | 4 | R | Uint32 unit kVA 3 decimal places If value=11720， PT=10,CT=10; then value=value*PT*CT= 11720*0.001*10*10=1172.0 kVA |
| 01F4H | 500 | Combined reactive electric energy | 4 | R | Uint32 unit kVarh 2 decimal places If value=120201， PT=10.0,CT=10; then value=value*PT*CT= 120201*0.01*10*10=120201 kVarh |
| 01F6H | 502 | Current first quadrant of reactive energy | 4 | R |  |
| 01F8H | 504 | Current second quadrant reactive energy | 4 | R |  |
| 01FAH | 506 | Current third quadrant of reactive energy | 4 | R |  |
| 01FCH | 508 | Current fourth quadrant reactive energy | 4 | R |  |
| 01FEH | 510 | A phase current Angle | 2 | R | Uint16 2 decimal places If value=9011,then value=9011*0.01=90.11° |
| 01FFH | 511 | B phase current Angle | 2 | R |  |
| 0200H | 512 | C phase current Angle | 2 | R |  |
| 0201H-0215H | 513-533 | 1-14 period of time Parameters setting information | 2 | R/W | 3# time list |
| 0216H-0249H | 534-585 | Related data of alarm 2 and alarm 3, see section 6.3.2 for details |  |  |  |
| 024AH-0267H | 586-615 | reserved |  |  |  |
| 0268H-0169H | 616-617 | Alarm status of alarm 2 and alarm 3, see section 6.3.2 for details |  |  |  |

Secondary Value Part 2

Table 2. Secondary Value

| Start Address （Hexadecimal） | Start Address （Decimal） | Variable | Length (Bytes) | R/W | Notes |
| --- | --- | --- | --- | --- | --- |
| 8800 | 34816 | Total active energy | 4 | R | Uint 32 unit kWh |
| 8802 | 34818 | Forward active energy consumption | 4 | R |  |
| 8804 | 34820 | Reversing active energy consumption | 4 | R |  |
| 8806 | 34822 | reserved | 4 | R | Uint 32 unit kVar |
| 8808 | 34824 | Forward reactive energy consumption | 4 | R |  |
| 880A | 34826 | Reversing reactive energy consumption | 4 | R |  |
| 880C | 34828 | reserved | 4 | R | Uint 32 unit kVAh |
| 880E | 34830 | Current total spike active energy | 4 | R | Uint 32 unit kWh |
| 8810 | 34832 | Current total peak active energy | 4 | R |  |
| 8812 | 34834 | Current total flat active energy | 4 | R |  |
| 8814 | 34836 | Current total valley active energy | 4 | R |  |
| 8816 | 34838 | Current total spike forward active energy | 4 | R |  |
| 8818 | 34840 | Current total peak forward active energy | 4 | R |  |
| 881A | 34842 | Current total flat forward active energy | 4 | R |  |
| 881C | 34844 | Current total valley forward active energy | 4 | R |  |
| 881E | 34846 | Current total spike reversing active energy | 4 | R |  |
| 8820 | 34848 | Current total peak reversing active energy | 4 | R |  |
| 8822 | 34850 | Current total flat reversing active energy | 4 | R |  |
| 8824 | 34852 | Current total valley reversing active energy | 4 | R |  |
| 8826 | 34854 | Current total spike forward reactive energy | 4 | R | Uint 32 unit kVar |
| 8828 | 34856 | Current total peak forward reactive energy | 4 | R |  |
| 882A | 34858 | Current total flat forward reactive energy | 4 | R |  |
| 882C | 34860 | Current total valley forward reactive energy | 4 | R |  |
| 882E | 34862 | Current total spike reversing reactive energy | 4 | R |  |
| 8830 | 34864 | Current total peak reversing reactive energy | 4 | R |  |
| 8832 | 34866 | Current total flat reversing reactive energy | 4 | R |  |
| 8834 | 34868 | Current total valley reversing reactive energy | 4 | R |  |
| 8836 | 34870 | Total active energy of A phase | 4 | R | Uint 32 unit kWh |
| 8838 | 34872 | Forward active energy consumption of A phase | 4 | R |  |
| 883A | 34874 | Reversing active energy consumption of A phase | 4 | R |  |
| 883C | 34876 | reserved | 4 | R | Uint 32 unit kVar |
| 883E | 34878 | Forward reactive energy consumption of A phase | 4 | R | Uint 32 unit kVar |
| 8840 | 34880 | Reversing reactive energy consumption of A phase | 4 | R |  |
| 8842 | 34882 | reserved | 4 | R | Uint 32 unit kWh |
| 8844 | 34884 | reserved | 4 | R |  |
| 8846 | 34886 | reserved | 4 | R |  |
| 8848 | 34888 | reserved | 4 | R |  |
| 884A | 34890 | Total active energy of B phase | 4 | R | Uint 32 unit kWh |
| 884C | 34892 | Forward active energy consumption of B phase | 4 | R |  |
| 884E | 34894 | Reversing active energy consumption of B phase | 4 | R |  |
| 8850 | 34896 | reserved | 4 | R | Uint 32 unit kVar |
| 8852 | 34898 | Forward reactive energy consumption of B phase | 4 | R | Uint 32 unit kVar |
| 8854 | 34900 | Reversing reactive energy consumption of B phase | 4 | R |  |
| 8856 | 34902 | reserved | 4 | R | Uint 32 unit kVar |
| 8858 | 34904 | reserved | 4 | R |  |
| 885A | 34906 | reserved | 4 | R |  |
| 885C | 34908 | reserved | 4 | R |  |
| 885E | 34910 | Total active energy of C phase | 4 | R | Uint 32 unit kWh |
| 8860 | 34912 | Forward active energy consumption of C phase | 4 | R |  |
| 8862 | 34914 | Reversing active energy consumption of C phase | 4 | R |  |
| 8864 | 34916 | reserved | 4 | R | Uint 32 unit kVar |
| 8866 | 34918 | Forward reactive energy consumption of C phase | 4 | R | Uint 32 unit kVar |
| 8868 | 34920 | Reversing reactive energy consumption of C phase | 4 | R |  |
| 886A | 34922 | reserved | 4 | R | Uint 32 unit kVar |
| 886C | 34924 | reserved | 4 | R |  |
| 886E | 34926 | reserved | 4 | R |  |
| 8870 | 34928 | reserved | 4 | R |  |
| 8872 | 34930 | Quadrant 1 Total Reactive Energy | 4 | R | Uint 32 unit kVar |
| 8874 | 34932 | Quadrant 2 Total Reactive Energy | 4 | R |  |
| 8876 | 34934 | Quadrant 3 Total Reactive Energy | 4 | R |  |
| 8878 | 34936 | Quadrant 4 Total Reactive Energy | 4 | R |  |
| 887A | 34938 | reserved | 4 | R |  |
| 887C | 34940 | reserved | 4 | R |  |

Primary Value (Real Value) Part 1

Table3.primary value

| Start Address （Hexadecimal） | Start Address （Decimal） | Variable | Length (Bytes) | R/W | Notes |
| --- | --- | --- | --- | --- | --- |
| 8000 | 32768 | Voltage of Aphase | 4 | R | float32 unit V |
| 8002 | 32770 | Voltage of B phase | 4 | R |  |
| 8004 | 32772 | Voltage of C phase | 4 | R |  |
| 8006 | 32774 | Voltage between A-B | 4 | R |  |
| 8008 | 32776 | Voltage between B-C | 4 | R |  |
| 800A | 32778 | Voltage between C-A | 4 | R |  |
| 800C | 32780 | Current of Aphase | 4 | R | float32 unit A |
| 800E | 32782 | Current of B phase | 4 | R |  |
| 8010 | 32784 | Current of C phase | 4 | R |  |
| 8012 | 32786 | Vector sum of 3-phase current | 4 | R |  |
| 8014 | 32788 | Active power of A phase | 4 | R | float32 unit kW |
| 8016 | 32790 | Active power of B phase | 4 | R |  |
| 8018 | 32792 | Active power of C phase | 4 | R |  |
| 801A | 32794 | Total active power | 4 | R |  |
| 801C | 32796 | Reactive power of A phase | 4 | R | float32 unit kVar |
| 801E | 32798 | Reactive power of B phase | 4 | R |  |
| 8020 | 32800 | Reactive power of C phase | 4 | R |  |
| 8022 | 32802 | Total reactive power | 4 | R |  |
| 8024 | 32804 | Apparent power of A phase | 4 | R | float32 unit kVA |
| 8026 | 32806 | Apparent power of B phase | 4 | R |  |
| 8028 | 32808 | Apparent power of C phase | 4 | R |  |
| 802A | 32810 | Total apparent power | 4 | R |  |
| 802C | 32812 | Power factor of A phase | 4 | R | float32 |
| 802E | 32814 | Power factor of B phase | 4 | R |  |
| 8030 | 32816 | Power factor of C phase | 4 | R |  |
| 8032 | 32818 | Total power factor | 4 | R |  |
| 8034 | 32820 | Frequency of power | 4 | R | float32 unit HZ |
| 8036 | 32822 | The average phase voltage | 4 | R | float32 unit v |
| 8038 | 32824 | Line voltage average | 4 | R |  |
| 803A | 32826 | Current average | 4 | R | float32 unit A |
| 803C | 32828 | Voltage imbalance | 4 | R | float32 unit 0.1% |
| 803E | 32830 | Current imbalance | 4 | R |  |
| 8040 | 32832 | residual voltage | 4 | R | float32 unit v |
| 8042 | 32834 | residual current | 4 | R | float32 unit A |
| 8044 | 32836 | A Power Angle | 4 | R | float32 unit 0.1° |
| 8046 | 32838 | B Power Angle | 4 | R |  |
| 8048 | 32840 | C Power Angle | 4 | R |  |
| 804A | 32842 | Phase A voltage angle | 4 | R |  |
| 804C | 32844 | Phase B voltage angle | 4 | R |  |

Primary Value (Real Value) Part 2

Table4.primary value

| Start Address （Hexadecimal） | Start Address （Decimal） | Variable | Length (Bytes) | R/W | Notes |
| --- | --- | --- | --- | --- | --- |
| 887E | 34942 | Total active energy | 4 | R | Float 32 unit kWh |
| 8880 | 34944 | Forward active energy consumption | 4 | R |  |
| 8882 | 34946 | Reversing active energy consumption | 4 | R |  |
| 8884 | 34948 | reserved | 4 | R | Float 32 unit kVar |
| 8886 | 34950 | Forward reactive energy consumption | 4 | R |  |
| 8888 | 34952 | Reversing reactive energy consumption | 4 | R |  |
| 888A | 34954 | reserved | 4 | R | Float 32 unit kVAh |
| 888C | 34956 | Current total spike active energy | 4 | R | Float 32 unit kWh |
| 888E | 34958 | Current total peak active energy | 4 | R |  |
| 8890 | 34960 | Current total flat active energy | 4 | R |  |
| 8892 | 34962 | Current total valley active energy | 4 | R |  |
| 8894 | 34964 | Current total spike forward active energy | 4 | R |  |
| 8896 | 34966 | Current total peak forward active energy | 4 | R |  |
| 8898 | 34968 | Current total flat forward active energy | 4 | R |  |
| 889A | 34970 | Current total valley forward active energy | 4 | R |  |
| 889C | 34972 | Current total spike reversing active energy | 4 | R |  |
| 889E | 34974 | Current total peak reversing active energy | 4 | R |  |
| 88A0 | 34976 | Current total flat reversing active energy | 4 | R |  |
| 88A2 | 34978 | Current total valley reversing active energy | 4 | R |  |
| 88A4 | 34980 | Current total spike forward reactive energy | 4 | R | Float 32 unit kVar |
| 88A6 | 34982 | Current total peak forward reactive energy | 4 | R |  |
| 88A8 | 34984 | Current total flat forward reactive energy | 4 | R |  |
| 88AA | 34986 | Current total valley forward reactive energy | 4 | R |  |
| 88AC | 34988 | Current total spike reversing reactive energy | 4 | R |  |
| 88AE | 34990 | Current total peak reversing reactive energy | 4 | R |  |
| 88B0 | 34992 | Current total flat reversing reactive energy | 4 | R |  |
| 88B2 | 34994 | Current total valley reversing reactive energy | 4 | R |  |
| 88B4 | 34996 | Total active energy of A phase | 4 | R | Float 32 unit kWh |
| 88B6 | 34998 | Forward active energy consumption of A phase | 4 | R |  |
| 88B8 | 35000 | Reversing active energy consumption of A phase | 4 | R |  |
| 88BA | 35002 | reserved | 4 | R | Float 32 unit kVar |
| 88BC | 35004 | Forward reactive energy consumption of A phase | 4 | R | Float 32 unit kVar |
| 88BE | 35006 | Reversing reactive energy consumption of A phase | 4 | R |  |
| 88C0 | 35008 | reserved | 4 | R | Float 32 unit kWh |
| 88C2 | 35010 | reserved | 4 | R |  |
| 88C4 | 35012 | reserved | 4 | R |  |
| 88C6 | 35014 | reserved | 4 | R |  |
| 88C8 | 35016 | Total active energy of B phase | 4 | R | Float 32 unit kWh |
| 88CA | 35018 | Forward active energy consumption of B phase | 4 | R |  |
| 88CC | 35020 | Reversing active energy consumption of B phase | 4 | R |  |
| 88CE | 35022 | reserved | 4 | R | Float 32 unit kVar |
| 88D0 | 35024 | Forward reactive energy consumption of B phase | 4 | R | Float 32 unit kVar |
| 88D2 | 35026 | Reversing reactive energy consumption of B phase | 4 | R |  |
| 88D4 | 35028 | reserved | 4 | R | Float 32 unit kWh |
| 88D6 | 35030 | reserved | 4 | R |  |
| 88D8 | 35032 | reserved | 4 | R |  |
| 88DA | 35034 | reserved | 4 | R |  |
| 88DC | 35036 | Total active energy of C phase | 4 | R | float 32 unit kWh |
| 88DE | 35038 | Forward active energy consumption of C phase | 4 | R |  |
| 88E0 | 35040 | Reversing active energy consumption of C phase | 4 | R |  |
| 88E2 | 35042 | reserved | 4 | R | Float 32 unit kVar |
| 88E4 | 35044 | Forward reactive energy consumption of C phase | 4 | R | float 32 unit kVar |
| 88E6 | 35046 | Reversing reactive energy consumption of C phase | 4 | R |  |
| 88E8 | 35048 | reserved | 4 | R | float 32 unit kVar |
| 88EA | 35050 | reserved | 4 | R |  |
| 88EC | 35052 | reserved | 4 | R |  |
| 88EE | 35054 | reserved | 4 | R |  |
| 88F0 | 35056 | Quadrant 1 Total Reactive Energy | 4 | R | float 32 unit kVar |
| 88F2 | 35058 | Quadrant 2 Total Reactive Energy | 4 | R |  |
| 88F4 | 35060 | Quadrant 3 Total Reactive Energy | 4 | R |  |
| 88F6 | 35062 | Quadrant 4 Total Reactive Energy | 4 | R |  |
| 88F8 | 35064 | reserved | 4 | R |  |
| 88FA | 35066 | reserved | 4 | R |  |